## 2023_V5.4 ARCH
SUMMARY OF PROPOSED ADDS / CHANGES - ARCH
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT | PAGE # | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
1 | Project Delivery | Caltech logo | - | Updated download link | 18 | Incorporated
2 | Project Delivery | Renders | All renderings developed for design to show diversity and inclusion. | Architectural Visualizations: Caltech strives to become an example of how a diverse and inclusive community, committed to equity and accessibility, permits individuals to thrive in fulfilling the Institute's mission of forefront research and education. Architectural visualizations in all formats, including computer-generated imagery, are to represent Caltech's diverse and inclusive community and Caltech's commitment to promoting and strengthening inclusion, diversity, equity and accessibility. | 18 | Incorporated | ADVANCEMENT - RENDER quality / size
3 | General Requirements | STC | a.Provide for sound control around offices, conference rooms, toilet rooms, mechanical rooms, and other sensitive areas. Required STC and other ratings to be coordinated with Caltech by room or are function. 1) STC requirement for typical rooms: i. STC 35 between office and corridor ii. STC 35 between lab and corridor iii. STC 40 between classroom and corridor iv. STC 40 between conference room and offices v. STC 40 between offices vi. STC 60 between vivarium space and its mechanical/equipment room (STC 50acceptable upon approved by Caltech PM) | a.Provide sound control around offices, conference rooms, toilet rooms, mechanical rooms, and other sensitive areas. Required STC and other ratings to be coordinated with Caltech by room or are function. 1) STC requirement for typical rooms: i. STC 35 between office and corridor ii. STC 35 between lab and corridor iii. STC 40 between classroom and corridor iv. STC 44 between conference room and offices v. STC 44 between offices vi. STC 50 between conference rooms vii. STC 50 between classrooms viii. STC 60 between vivarium space and its mechanical/equipment room (STC 50acceptable upon approval by Caltech PM) | 19 | Incorporated
4 | General Requirements | Laboratory flooring |  | b. Standard Laboratories: Provide the following: 1) Vinyl Flooring: Solid-pattern type premium floor tile (12 inch by 12 inch) equivalent to a. Armstrong Premium Excelon. b. Forbo c. Tarkett 2) Rubber Flooring: tile flooring equivalent to a. Forbo b. Nora c. Tarkett | 19 | Incorporated
5 | General Requirements | Laboratory phones |  | Phone to be installed in a CBC and ADA accessible location, at a CBC and ADA accessible height. | 19 | Incorporated
6 | General Requirements | Paper towel dispensers |  | 17) Provide roll paper towel dispenser at all lab sinks. Where not possible to mount a roll paper towel dispenser, provide countertop folded paper towel dispenser. Product selection to be approved by Caltech project PM and the Director of Facilities Operations. Roll paper towel dispenser option 1: Scott® Pro Automatic Hard Roll Towel Dispenser PRODUCT CODE #35614 (Grey core) Roll paper towel dispenser option 2: Scott® Control Slimroll Electronic Towel Dispensers PRODUCT CODE #47260 Folded paper towel dispenser: Tork Xpress Countertop Multifold Hand Towel Dispenser”, in black #302028 or brushed stainless steel #302030. 16) Folded paper towels: project to provide first and second refill of: “Tork Premium Multifold Hand Towel” #420580. | 20 | Incorporated
7 | General Requirements | Worksurface height | 19) Bench height to be 36” nominal finished.Desk height to be 30” nominal finished. | 19) Bench height to be 36” nominal finished. Provide 34” bench height in designated accessible areas of the lab. Coordinate with PD&C Architect on accessibility provisions for each lab. Desk height to be 30” nominal finished. | 20 | Incorporated
8 | General Requirements | Existing conditions |  | 4) For all projects: Demo all existing unused systems, utilities and associated supports, and patch and repair surfaces. In exposed ceiling areas: paint all visible surfaces including utilities and associates supports. | 22 | Incorporated
9 | General Requirements | Markerboards |  | i. Markerboards: acrylic, melamine or similar whiteboards are not acceptable. Acceptable whiteboard types: back painted glass, porcelain enamel steel. Discuss with PM any deviations, including wall-talkers specifications. | 22 | Incorporated
10 | General Requirements | Restrooms - tile grout |  | g.Restrooms: Tile grout: white or black grout on floors and walls is not allowed. | 22 | Incorporated
11 | General Requirements | ECCR DAS radio communication requirements |  | 18. ECCR DAS radio communication requirements | 22 | Incorporated
12 | Project Delivery | Architectural Visualizaions | All renderings developed for design to show diversity and inclusion. | All renderings developed for design to show diversity and inclusion. Architectural Visualizations: Caltech strives to become an example of how a diverse and inclusive community, committed to equity and accessibility, permits individuals to thrive in fulfilling the Institute's mission of forefront research and education. Architectural visualizations in all formats, including computer-generated imagery, are to represent Caltech's diverse and inclusive community and Caltech's commitment to promoting and strengthening inclusion, diversity, equity and accessibility. | 23 | Incorporated
13 | Project Delivery | Campus single line drawings |  | The same applies to all other building systems and utilities. | 23 | Incorporated
14 | 01 58 00 | Project Identification | b. Graphic image shall be furnished by Design Professional following Caltech standard. List title of Project team members including but not limited to: Names of Caltech personnel, Design Professionals, Mechanical Consultant, Plumbing Consultant, Electrical Consultant, Structural Consultant, and Contractor. c. Erect on site at location to be determined by Caltech. | b. Coordinate with Caltech PM on signage design standard and sign locations. Graphic image shall be furnished by Design Professional following Caltech standard. All text should be legible, drawings to be ‘presentation style’ easily legible bny the public.. List title of Project team members including but not limited to: Names of Caltech personnel, Design Professionals, Mechanical Consultant, Plumbing Consultant, Electrical Consultant, Structural Consultant, and Contractor. c. Erect on site at locations to be determined by Caltech. | 36 | Incorporated
15 | 01 78 00 | Closeout Submittals | 3) Provide list of finishes and vendors of the following items listed below to the CIT Project Manager in one document. This in addition to submittals required by the appropriate specification section. i. Paints, Carpets, Wall Base, Ceiling Tiles, Resilient Flooring, Furnishings, Equipment, etc. | 3) Provide list of finishes and vendors of the following items listed below to the CIT Project Manager in one document. This in addition to submittals required by the appropriate specification section. Organize the information per room or per space, to allow for CIT to reference in future repair or renovation work: i. Paints, Carpets, Wall Base, Ceiling Tiles, Resilient Flooring, Furnishings (incl. furniture list, millwork and furniture finishes), Equipment, Lighting, etc. | 37 | Incorporated
16 | 01 78 00 | Closeout Submittals - Approved As-builts | PDF | PDF, Excel | 38 | Incorporated
17 | 01 78 00 | Closeout Submittals - Approved Permit set and Approved As-Builts | PDF and CADD | PDF, CAD, and Revit where applicablePDF and CADD | 38 | Incorporated
17 | 01 78 00 | Closeout Submittals - Photos |  | See table. | 38 | Incorporated | Photographic documentation already a requirement before v5.4, this just references the document so as to not miss the requirement
18 | 01 78 00 | Closeout Submittals | (3) all electronic closeout deliverables shall be provided on CD or DVD with appropriate labeling to include project name, building name and date (e.g. vendor/consultant name, CIT project #, content of disk, release date of disk, etc. | (3) all electronic closeout deliverables shall be provided with appropriate labeling to include project name, building name and date (e.g. vendor/consultant name, CIT building number, CIT project #, etc. | 39 | Incorporated
19 | 02 00 00 | Existing Conditions |  | d. Coordinate with Caltech PM and Caltech Asset Manager for all assets identified for demolition. Provide an asset tag list of all assets scheduled for decommissioning and demolition. DO NOT DEMO assets without informing CIT PM AND CIT Asset Manager. | 40 | Incorporated
20 | Signage | Signage Warranty | d. Warranties 1) See Appendix II, submittal register | Check with Project Manager and Space Information Manager for signage warranty requirements per project. | 101 | Incorporated | forthcoming in later DG update: All exterior and interior signage is required to have a 5-year warranty on materials and workmanship.
21 | Signage | Restroom Signage | All toilet rooms that are accessible to persons with mobility impairments must include the International Symbol for Accessibility (ISA) on door and wall signs. | Remove, unnecessay on door, as covered by CDC + ADA | 101 | Incorporated
22 | Signage | Restroom Signage | Room number shall be on wall above the corresponding wall sign. | Remove, covered by signage guidelines | 101 | Incorporated
23 | Signage | Interior Signage | Laboratory Signs: Manufacturer and design to be selected by Design Professional. | Laboratory Signs: Manufacturer and design to be selected by Design Professional and approved by Caltech PM | 101 | Incorporated
24 | 09 67 23 | Resinous flooring |  | Dex-o-Tex | 101 | Incorporated
25 | Restrooms | All gender restroom | RR – Unisex or Single-User or All Gender restroom | (1) RR – All Gender or Single-User or All Gender restroom | 104 | Incorporated
26 | Signage | Signage stakeholders | - | Added: Inclusion and Diversity | 104 | Incorporated
27 | Signage | Interior Signage |  | Caltech has a sign standard for room number signs. See Apprendix XXVI. Any deviation from the Caltech standard should be determined in consultation with and approved by the Caltech Design & Construction Space Information Manager, Architect, and Inspector. | 104 | Incorporated
28 | Signage | Interior Signage | Sign, materials, shapes, and dimensions must be approved by the Caltech Space Information Manager prior to production. | Shop drawings identifying sign content, materials, shapes, and dimensions must be approved by the Caltech Space Information Manager prior to production. | 104 | Incorporated
29 | 10 11 00 | Visual Display Units |  | 3. Product Requirements: a. Markerboards: Porcelain-enamel-clad steel with low gloss matte finish and magnet capability. Acceptable whiteboard types: back painted glass, or porcelain-enamel-clad steel with low gloss matte finish and magnet capability. Discuss with PM any deviations, including wall-talkers specifications. Acrylic, melamine or similar whiteboards are not acceptable. | 105 | Incorporated
30 | 10 21 00 | All-gender partitions | Partitions shall be stainless steel ceiling-hung with concealed hardware. No partition gaps allowed at either side of the privacy door or between dividing panels or at wall. | 3. Product Requirements: a. CIT Project Manager to approve partitions, particularly for all-gender restrooms. b. Acceptable product for all-gender partitions: Scranton Products Aria, or approved equal. c. At non all-gender spaces: Partitions shall be stainless steel ceiling-hung with concealed hardware. Floor-and-ceiling anchored if ceiling-hung is not feasible. d. No partition gaps allowed at either side of the privacy door or between dividing panels or at wall. Added to that, for all-gender spaces, minimize gaps at ceiling or floor (1/2" max at ceiling, 1/4" max at floor) or any location where privacy may be breached. Coordinate with Caltech PM on additional requirements in all-gender spaces i.e. ventilation, F&LS devices, etc. | 117 | Incorporated
31 | 12 00 00 | Roller Shades | 1. Roller Shades: For exterior fenestration, provide roller shades; manual or electric to be determined based on Project requirements. For renovation projects, consider existing building shade type and color for matching or coordinated exterior look. | 1. Roller Shades: For all window shades, review with Caltech before final selections. For exterior fenestration, provide roller shades; all shades should be manual with any deviation to be approved by PDC Architect. For renovation projects, consider existing building shade type and color for matching or coordinated exterior look. Review with Caltech options of window shade systems and their integration with the façade or fenestration in order to select the most adequate approach per Project and condition. Design is to minimize unusable space between shade and envelope and minimize the likelihood of failure. Prior to approval, and at project close-out: provide Caltech with documentation in print, presentation, or video, that show operations instructions and outline any user practices that should be avoided or that have been found in the past to cause the shade system to fail. | 126 | Incorporated
32 | 12 00 00 | Furnishings - Epoxy Resin Work Surface | f. Color: Black Onyx or Grey. | f. Color: Black Onyx or Grey, grey recommended. | 139 | Incorporated
33 | 12 00 00 | Furnishings - Epoxy Resin Work Surface |  | n. Fundermax work surface can be used in lieu of epoxy resin work surface in certain labs. Coordinate with Caltech PM on use of Fundermax work surface. | 140 | Incorporated
34 | 12 00 00 | Furnishings - Task Lights |  | e. Task lights to have dedicated power outlets, horizontally oriented and located as close as possible to underside of upper cabinets. | 145 | Incorporated | requirement is not new, but added here as it is common miss lately.
35 | 14 00 00 | Conveying Equipment |  | c) Comply with all applicable California Code of Regulations including Title 24. | 158 | Incorporated
36 | Revit | Revit version | The version of Autodesk Revit, defined by the design team, used from the start of the project must remain a constant throughout the life of the project. | The version of Autodesk Revit, defined by the design team, and subsequent upgrades should be agreed upon with CIT. | 359 | Incorporated
37 |  | AIA reference typo |  | 2013 | 360 | Incorporated
38 |  | Deliverable formats |  | SUPPORT FILES: Deliver all assets necessary to recreate output that matches hard copy submittals. Support files include, but are not limited to, the following: AutoCAD native drawing files (.dwg), Images, PDF, excel (.xlsx), and any other External Links. Deliver files to the Owner free of any copyrighted or other material whose distribution is prohibited. | 360 | Incorporated | CONTRACTS - ALEX - ALIGN
39 |  | Signage standard design | Sign images | Delete, and issue interior signage package as an appedix to the Design Guidelines | 105, 106, 107, 108 | Incorporated
40 | All | Planning Design & Construction | All instances of D&C or Design & Construction | Changed to PD&C or Planning Design & Construction | All | Incorporated
41 |  | Interior Signage Standards | - | New Appendix XXVI: 2024 Caltech Wayfinding - Interior Signage | APPENDIX XXVI | Incorporated
42 |  | Exterior Signage Guidelines | - | New Appendix XXVII: 2024 Caltech Wayfinding - Exterior Signage | APPENDIX XXVII | Incorporated
43 |  | Exposed Ceilings | No Content | Demo and clean up unused utilities and associated supports. Paint new utilities and associated supports. Deviation to be approved by PM. |  | Incorporated
44 |  | LOD 500 requirment | "LOD 500 per AIA G202" | LEVEL OF DEVELOPMENT (LOD): Final model deliverables are to be agreed upon with CIT, and follow the latest AIA Document G202TM . |  | Incorporated | ALIGN WITH BIM STANDARDS DOC AIA G202 does not require LOD500
45 |  | DAS ECCR reference requirements | - |  | APPENDIX 28 | Incorporated
46 | 07 52 00 and 07 56 00 | Roof repairs | - | a. For all repairs, testing for compatibility of products is required. Coordinate with CIT Roofing shop. Recommended roofing repair products: 1) Castagra Ecodur One – for full coatings of existing roofs. 2) Castagra Ecodur Plus – for localized repairs. | 58, 62 | Incorporated

## 2023_V5.4 MECH-PLUMB
SUMMARY OF PROPOSED ADDS / CHANGES - MECH-PLUMB
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT | PAGE # | UPDATE STATUS
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7
1 | 23 34 00.5 | Lab exhaust stack height | 10'-0" minimum height requirement. | Provide wind analysis and computational fluid dynamics (CFD) modeling required to validate stack height, velocity, and cfm. Minimum discharge height shall be 15 feet above roof when stack height is calculated. | 206 | Incorporated
2 | 11 53 13.10 | Pre-piped and pre-wired hoods | Hoods shall be pre-piped and pre-wired to top, or as shown. | removed "or as shown". | 115 | Incorporated
3 | 23 00 00.1 | Humidifier design criteria outdoor conditions | 20.8 degree F wet bulb | 35 degree F dry-bulb, 2% RH | 182 | Incorporated
4 | Outline Plumbing Piping Requirements | Item P22 - special lab gases (non-high purity) | Brazed and press joints acceptable for helium service piping. | Piping serving helium shall be brazed no exceptions whatsoever. | NA | Incorporated
5 | 22 00 00 - Plumbing | Existing backflow preventers | Not included. | Existing backflow preventers noted to be removed and dismantled in Construction Documents shall be salvaged. Clean, package, label, and deliver to Caltech per Divisions 1 and Division 2 specifications. Provide documentation of cleaning. | 161 | Incorporated
6 | 23 00 00 | Existing backflow preventers | Not included. | Existing backflow preventers noted to be removed and dismantled in Construction Documents shall be salvaged. Clean, package, label, and deliver to Caltech per Divisions 1 and Division 2 specifications. Provide documentation of cleaning. | 178 | Incorporated
7 | Outline Plumbing Piping Requirements | NIBCO ball valves. Comment number 2 at bottom of spreadsheet. | Not included. | T-585-70-66 is only be acceptable for ICW&IHW and other non-potable applications as it is not a lead-free valve. T-585-66-LF is a lead-free valve and shall be required on the potable water system (DCW + DHW). | NA | Incorporated
8 | Outline Plumbing Piping Requirements | Item P9, P10A, P12, P16, P17. Cast iron piping specification reference | CISPI Standard 310 | CISPI Standard 301. | NA | Incorporated
9 | Control Valve selection table | Item 4 Heating hot water | Heating hot water (CHW + AHU). CHW symbol. | Application media (column B) description has been revised to "FCU + AHU". CHW reference in symbol (column C) has been removed. | NA | Incorporated
10 | Outline Plumbing Piping Requirements | Pipe hangers and support spacing. | Excel file includes copies of tables in "Pipe Hanger & Support Spacing" tab. | Removed "Pipe Hanger & Support Spacing" tab. | NA | Incorporated
11 | Appendix X - Plumbing Piping Requirements | Pipe hangers and support spacing. | Piping Support Hanger Rod Table, Piping Support Spacing Table | Removed tables. | 345 | Incorporated
12 | 11 53 13.10.a | Laboratory fume hood DI water piping | Not included. | DI water piping in fume hood shall be 316L SS steel tubing. Polypro piping is not acceptable. | 115 | Incorporated
13 | Outline Plumbing Piping Requirements | Item P24 - Acid Waste & Acid Vent (gravity) (option 1), direct buried, below grade only | CPVC material and specification | Option removed | NA | Incorporated
14 | Outline Plumbing Piping Requirements | Item 29 - GF fuseal product for acid waste & vent, above ground, inside wall cavities and concealed shaft spaces. | Not included. | Added GF fuseal product. | NA | Incorporated
15 | Outline Plumbing Piping Requirements | Item 31 - GF Piping Systems' mechanical joints for acid waste & vent, above ground, inside active return air plenums in visible and accessible spaces only. | Not included. | Added GF piping systems' mechanical joints product. | NA | Incorporated
16 | Appendix XX | Process Cooling Water Heat Exchanger Details | Did not include flow meter in house chilled water side | Added flow meter and unions in house chilled water side. | 398-399 | Incorporated
17 | Plumbing Fixtures and Products Table | Item PF-15 Mop sink faucet | Not included. | Chicago faucets model 897-CPP sink faucet with integral check valves and vacuum breaker, chrome plated finish | NA | Incorporated
18 | Control Valve selection table | Actuator position and features note for heating control valves | Not included. | Added note #3: Heating hot water control valves shall fail to close with spring return | NA | Incorporated
19 | Outline Plumbing Piping Requirements | Item 30 - GF fuseseal product for acid waste & vent, above ground, inside active return air plenums | Not included. | Added GF fuseal 25/50 product. | NA | Incorporated
20 | 23 35 00.1.b - Domestic & Industrial Water Heat Exchangers | Single wall vs double wall specification | Double wall required for both domestic and industrial water heat exchangers | Double wall required for domestic application. Single wall is acceptable for industrial application. | 177 | Incorporated
21 | 23 05 93.2.e - TAB specification | Acceptable air and hydronic balance quantities. | 1% variation required for lab areas and 5% for all others. | 5% variation required for labs and all other areas. Additionally, for lab areas, air balance shall not be below 1%. | 193 | Incorporated
22 | General Requirements item 14 - Asset and BMS naming standards | Asset and BMS naming standards link. | http broken link | Updated link to https. | 16 | Incorporated
23 | Outline Mechanical and HVAC Hydronic Piping requirements | Item H3, H4 insulation material | 1) Non-plenum rated applications: Trymer 2000XP, 3) Plenum rated applications: Closed-cell phenolic insulation similar to Trymer Supercel | 1) Outdoor applications: Trymer 2000XP, 3) Indoor applications (non-plenum rated and plenum rated): closed cell, phenolic insulation, with flame spread less than or equal to 25, smoke developed less than or equal to 50, meet ASTM E84 test method, similar to Trymer Supercel. | NA | Incorporated
24 | 23 07 19 HVAC Piping Insulation. 1.7-8 | Steam and steam condensate insulation in tunnels | insulation material, thickness, and jacket specification | Removed sentences 7 and 8. These specifications are included in "Outline Mechanical and HVAC Hydronic Piping Requirements" Excel matrix. | 191 | Incorporated
25 | Plumbing Fixtures and Products Table | Item P17 - Storm drainage and roof drain pipe and pipe fittings above ground | Husky SD4000 no-hub couplings | Change couplings to Husky SD2000. | NA | Incorporated
26 | Appendix XX | AHU chilled water coil piping detail | Not included. | New detail. | 393 | Incorporated
27 | Plumbing Fixtures and Products Table | Kitchenette sink | Model LRAD | Model ELUHAD to match undermount description. Minimum depth: 5.375". | NA | Incorporated
28 | 22 05 13.8. | VFD bypass | Three (3) contactor bypass (only where requested by CIT) | Three (3) contactor bypass feature on equipment without N+1 redundancy. | 163 | Incorporated
29 | Plumbing Fixtures and Products Table | Item P-09 Lavatory mixing faucet | battery operated | Added note in "Means & methods and installation requirements" column: For use only were allowed. Obtain CIT facilities engineer approval. | NA | Incorporated
30 | Plumbing Fixtures and Products Table | Item P-09b Lavatory mixing faucet | Not included. | New item. Hardwire type faucet. For new construction applications. | NA | Incorporated
31 | Plumbing Fixtures and Products Table | Item PC-24 Undercounted mixing valve | Not included. | New item. Guardian/Watts Series LFUSG-B-M2 | NA | Incorporated
32 | Outline Mechanical and HVAC Hydronic Piping requirements | Pipe hangers and support spacing. | Excel file includes copies of tables in "Pipe Hanger & Support Spacing" tab. | Removed "Pipe Hanger & Support Spacing" tab. | NA | Incorporated
33 | 23 07 19.9 HVAC Piping Insulation | Chilled water insulation | Chilled and cold-water piping subject to surface condensation, including medium temperature chilled/cooling water piping serving radiant devices (active chilled beams, ceiling panels, etc.), shall only be insulated with closed cell insulation materials. No fiberglass insulation shall be allowed for the chilled water piping, or pipes carrying fluids below ambient temperature. | Add the following sentence: For outdoor applications, polyisocyanurate rigid foam insulation similar to Trymer 2000XP is acceptable. | 196 | Incorporated
34 | Outline Plumbing Piping Requirements | Item P10 - W& V and SD (option #2) | CPVC material and specification | Option removed | NA | Incorporated
35 | Appendix X1 - General Mechanical Requirements | Item 24 - laboratory equipment cooling | Not included. | Laboratory equipment shall never be connected to campus chilled water. A water-to-water heat exchanger shall be utilized. | 347 | Incorporated
36 | 23 00 00.3 | Electrical outlet and industrial water hose bib near AHU | Not included. | Provide electrical outlet and industrial water hose bib within 6 feet of AHU. | 180 | Incorporated
37 | 23 09 00.2.I | Network Manager (JACE) | Distech or Vykon JACE 8000 series listed as acceptable manufacturers | Removed "Distech or" from Network Managers (JACE). Only Vykon JACE 8000 Series is acceptable. | 223 | Incorporated
38 | 23 09 00.3.i.20 | VFD and DDC controllers comissioning | Not included. | VFD and DDC controllers shall be field tested for self-recovery mode upon power failure. VFDs and DDC controllers shall not reset to manufacturer default programing. Self-recovery mode shall be set to project programming. | 235 | Incorporated
39 | 23 00 00 - HVAC Systems.1.Design Criteria. A | Outdoor summer design conditions | 99 degree F dry-bulb, 80 degree F wet-bulb | 107 degree F dry-bulb, 72 degree F wet-bulb | 179 | Incorporated
40 | Appendix XX - Standard Details | 2-way TCV and 3-way TCV reheat coils | Included detail without hangers | Add two hangers in between hydronic trim components. | 373, 374 | Incorporated
41 | 22 00 00 - Plumbing systems. 3.a. Special / Laboratory Plumbing System Criteria | Compress air dew point | -38 DF dew point | Revise compress air dew point from central plant to 38F. | 162 | Incorporated
42 | 22 07 19.6. Pipe insulation schedule | Plumbing insulation thickness | Insulation thickness table | Schedule removed. Mechanical Piping Table link removed. Provide plumbing piping insulation per "Outline Plumbing Piping Requirements" Excel matrix and California Energy Code. When there is conflict, whichever is more stringent prevails. | 166 | Incorporated
43 | Outline Mechanical and HVAC Hydronic Piping Requirements | Insulation sizes | "See insulation thickness table in the appendix section" | Per California Energy Code | NA | Incorporated
44 | Plumbing Fixtures and Products Table | Item PF-01 Floor mounted water closets | Not included. | Added note in "Means & methods and installation requirements" column: For use only were allowed. Obtain CIT facilities engineer approval. | NA | Incorporated
45 | Plumbing Fixtures and Products Table | Item PF-02 Wall hung water closet | Not included. | Added note in "Means & methods and installation requirements" column: For new construction applications. | NA | Incorporated
46 | 23 05 13.8. | VFD bypass | Three (3) contactor bypass (only where requested by CIT) | Three (3) contactor bypass feature on equipment without N+1 redundancy. | 184 | Incorporated
47 | 23 09 00. 2.qq.3.d | VFD bypass | No exceptions | Provide bypass feature on equipment without N+1 redundancy. | 230 | Incorporated
48 | 26 29 23.1.d.4 | VFD bypass | No exceptions | Provide bypass feature on equipment without N+1 redundancy. | 270 | Incorporated
49 | Appendix XX | Isolation valve installation detail | Not included. | Added new detail | 387 | Incorporated
50 | Plumbing Fixtures and Products Table | Item PF-16 shower stall control valve | Not included. | Added specification for shower stall control valve | NA | Incorporated
51 | 23 07 19 HVAC Piping Insulation. 1.5 | Domestic cold and industrial cold water insulation | Required at tunnels, roofs and exposed to elements | Sentence removed. | 169 | Incorporated
52 | Plumbing Fixtures and Products Table | Item PF-14 hydration station / drinking fountain | single station, refrigerated model | removed single station, refrigerated model. Added two station, non-refrigerated model and option for refrigerated model | NA | Incorporated

## 2023_V5.4 LANDSCAPE
SUMMARY OF PROPOSED ADDS / CHANGES - LANDSCAPE
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT | PAGE # | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
1 | Appendi XIX | Plant pallette |  | Updated appendix and plant pallette | 361 | Incorporated
2
3
4
5
6
7
8
9
10

## 2023_V5.4 ELECTRICAL
SUMMARY OF PROPOSED ADDS / CHANGES - ELECTRICAL
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT | PAGE # | UPDATE STATUS
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
| 12 35 53 – Laboratory Casework | Lighting Color Temperature | Task lights to have color temperature to be 3500K. | Task lights to have color temperature to match the color temperature of the room. | 138 | Incorporated
1 | 26 00 00 - 1 - e - 13 |  |  | Provide between floors of electrical rooms and or electrical closets the following: 4 ea. 5.5” openings for future 5” conduits and 5 ea. 2.5” openings for future 2” conduits | 243 | Incorporated
2 | 26 10 00 - 5 - c |  |  | Electric Meter shall have BMS connectivity | 264 | Incorporated
3 | 26 05 33 - 4 - n |  |  | Provide at minimum 2ea. 5” spare conduits for the medium voltage feeders, one per medium voltage feeder | 257 | Incorporated
4 | 26 05 33 - 4 - o |  |  | Provide at main electrical room at least 2ea. 2” spare conduits for building controls and communications from the nearest building and/or as requested by Caltech | 257 | Incorporated
5 | 26 11 10 - 1 - a |  |  | Provide pulling underground vault for all pad mount equipment | 262 | Incorporated
6 | 26 00 00 - 1 - e - 13 |  |  | Provide epoxy sealer paints for floors, sealer paint for walls and ceiling for all main electrical rooms. This is to minimize concrete, plaster, or other dusts into electrical gear. | 243 | Incorporated
7 | 26 05 13 - 3 - a |  |  | All primary 2,400V & 4,160V cables shall be minimum 5kV, 500Kcmil shielded, single copper conductor. | 251 | Incorporated
8 | 26 05 33 - 2- e |  |  | Grounding: All conduits shall have a green ground onductor sized per NEC requirements | 256 | Incorporated
9 | 26 05 13 - 4 - v |  |  | Provide at all medium voltage connections (splices, switches, etc.) with removable dead break elbows with incorporated test point. Elastimold splice (P/N K656I-W0X) or approved by electrical engineer. | 252 | Incorporated
10 | 26 24 00 - 1 - i |  |  | 120/240 volt, 1 phase, 3 wire and 208Y/120V, 3 phase, 4 wire panelboards furnished under this section of the specifications shall be Square D, EATON, GE or Caltech approved equal. 208Y/120V panelboards shall have a minimum 225 amp bus with maximum of 60 circuits, integrated symmetrical short circuit rating of 22,000 amperes or as required in the arc flash studies, or per calculations. | 266 | Incorporated
11 | 26 24 00 - 1 - j |  |  | 480Y/277V, 3 phase, 4 wire panelboards furnished under this section of the specifications shall be Square D, EATON, GE or Caltech approved equal. 480Y/277V panelboards shall have a minimum 225 amp bus with maximum of 60 circuits, with minimum integrated symmetrical short circuit rating of 65,000 amperes, or as required in the arc flash studies, or per calculations. | 266 | Incorporated
12 | 26 00 00 - t - 1 |  |  | In addition to Manufacture nameplates, all equipment (including but not limited to panels, switchboards, motors, motor control centers, pull boxes, manholes, feeders, splice boxes, VFDs, transformers, inverters, switches, capacitors, etc.) provided shall be furnished with engraved nameplates, tags, and/or other identification method described below. | 247 | Incorporated
13 | 26 11 16 - 4- b |  |  | Square D Power-Zone IV draw-out type utilizing Master pact NW type power lover voltage circuit breakers with Micrologic 6.0P or equal by EATON and GE. |  | Incorporated
14 | 26 51 00 Interior Lighting | Lighting Color Temperature | (1) General illumination LED lighting shall be 3500K with maximum CRI available (2) Color Rendering Index shall be ≥ 80 | (1) General illumination LED lighting shall be 4000K. If spaces have existing 3500K lamps, coordinate with CIT PM and Architect on color selection (2) Color Rendering Index shall be highest available, with a minimum of 80 | 290 | Incorporated
15 | 27 51 00 Interior Lighting | Lighting Color Temperature | Lamps should be 3500K with highest CRI available. | Lamps should be 4000K with highest CRI available. If spaces have existing 3500K lamps, coordinate with CIT PM and Architect on color selection. | 291 | Incorporated
16
17
18

## 2023_V5.4 SUSTAINABILITY
SUMMARY OF PROPOSED ADDS / CHANGES - ENERGY & SUSTAINABILITY
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT | PAGE # | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
1
2
3
4
5
6
7
8
9
10
11

## 2023_V5.4 IMSS
SUMMARY OF PROPOSED ADDS / CHANGES - EH&S
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT for V5.4 | PAGE # | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
1
2
3
4
5
6
7
8
9
10

## 2023_V5.4 EHS
SUMMARY OF PROPOSED ADDS / CHANGES - EH&S
ITEM # | DG SECTION # | TOPICS | CONTENT IN V5.3 | PROPOSED CONTENT for V5.4 | PAGE # | UPDATE STATUS | Comments
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
1 | 21 00 00.18 | Fire extinguishers | No manufacturer listed | Amerex 5 lb | 160 | Incorporated | Jason Gomez / Amarex 5lb
2
3
4
5
6
7
8
9
10